## Refrigerant & Oil Charge
Optyma iCO2 model OP-MPAM005COP04G
Refrigerant and Oil Charge Calculation
vers 2023.01.31 |  |  |  |  | fill in blue cells
|  |  |  | Refrigerant Charge | Max Ambient Temp. | degC | 32
kg
Condensing Unit Base Line Charge |  |  |  | 2.15 | Oil Boost Speed | Oil Addition | comment
[5 empty] | RPM | g
Liquid Line Diam | Internal volume | Liquid Line Length | Average density | Refrigerant Charge | No Boost | 730 | Good Oil Return Not Guaranteed
inches | L/m | m | kg/L | kg | 3000 | 730 | Good Oil Return Not Guaranteed
3/8'' | 0.05 | 20 | 0.8 | 0.8 | 4500 | 490 | OK
1/4'' | 0.018 | 0 | 0.8 | 0 | 5600 | 490 | OK
Total Liquid Line Charge |  |  |  | 0.8 | oil return calculation assume suction line D3/8
Evaporator | Internal volume | Set Point | Average density | Refrigerant Charge
Id | L | degC | kg/L | kg
1 | 3 | -5 | 0.14876 | 0.44627
2 | 3 |  |  | 0.44627
3 | 2 |  |  | 0.29751
4 | 0 |  |  | 0
Total chage required by evaporator |  |  |  | 1.19
Total Allowable Evaporator Charge |  |  |  | 1.19
Total evaporator charge should never exceed 1.35 kg. This is to protect the condensing unit of being overcharged. Overfilling the system may risk of liquid return to compressor through bypass valve when running. Overfilling the system may risk in pressure increase and release of refrigerant through the receiver relief valve during standstill.
Total system Charge = CDU + Liquid Line + Evaporator charge |  |  |  | 4.14

## a (hidden)
Set Point | Average density
degC | kg/L
-5 | 0.14876

## b (hidden)
Original oil calculation file was limitied to
+ 2 evaporator
+ of 2 liters
+ discrete evaporating temperature -20 / -15 / -10 ... / +10
In this tab we do the mapping between user tab 'Refrigerant Charge" and calculation tab
We consider that calculation for 2 evaporator also applied for 3 or 4 evaporator
Tevap | degC | -5
Num evap | - | 2
Calculation result show oil addition
but we need to increase oil volume
Evap total vol | L | 8
oil addition | g | 300
| Amount of additional oil | Amount of additional oil | comment
oil boost | For 2 L evap | For installation
no boost | 430 | 730 | Good Oil Return Not Guaranteed
3000 | 430 | 730 | Good Oil Return Not Guaranteed
4500 | 190 | 490 | OK
5600 | 190 | 490 | OK

## c (hidden)
＜input＞ |  |  | <output>
|  |  | Oil return control set value | Amount of additional oil | comment
Evaporator unit (≦2.0L/unit) | 2 | unit | no boost | 430 | Good Oil Return Not Guaranteed
Thermo OFF set temperature | -5 | ℃ | 3000rpm(Default) | 430 | Good Oil Return Not Guaranteed
Highest operating ambient temperature | 32 | ℃ | 4500rpm | 190 | OK
|  |  | 5600rpm | 190 | OK
※Piping inner diameter 7.52 mm, length 20m(one side)

## d (hidden)
Judgment of ambient temperature at which oil can be returned | [7 empty] | Judgment of establishment conditions | [7 empty] | For display
2200rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 2200rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | Evaporator unit (≦2.0L/unit) |  | 1 | 2
| Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0 |  | Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0 | Oil return control set value | 2200rpm
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | 3000rpm
Thermo OFF set temperature | -25 | 28.2548 | 19.8604 |  |  |  |  | Thermo OFF set temperature | -25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4500rpm |  | 430 | 190
| -20 | 29.0591 | 20.747 | [5 empty] | -20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5600rpm |  | 430 | 190
| -15 | 32.1256 | 22.9774 | [5 empty] | -15 | 0 | 0 | 0 | 0 | 0 | 0
| -10 | 34.8165 | 29.6756 | [5 empty] | -10 | 0 | 0 | 0 | 0 | 0 | 0
| -5 | 35.8138 | 32.929 | [5 empty] | -5 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 36.4923 | 33.7439 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 37.6552 | 34.6974 | [5 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0
3000rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 3000rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2
| Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0 |  | Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8
Thermo OFF set temperature | -25 | 36.1995 | 32.1451 | 15.9985 | 15.9985 |  |  | Thermo OFF set temperature | -25 | 0 | 0 | 0 | 0 | 0 | 0
| -20 | 36.5238 | 32.7213 | 16.1887 | 16.1887 |  |  |  | -20 | 0 | 0 | 0 | 0 | 0 | 0
| -15 | 41.1341 | 36.8933 | 16.1887 | 16.1887 |  |  |  | -15 | 0 | 0 | 0 | 0 | 0 | 0
| -10 | 44.7132 | 36.9873 | 25.3817 | 25.3817 |  |  |  | -10 | 0 | 0 | 0 | 0 | 0 | 0
| -5 | 45.3961 | 37.2312 | 30.1769 | 30.1769 |  |  |  | -5 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 45.8213 | 37.7148 | 31.6767 | 31.6767 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 46 | 43.9367 | 32.5699 | 32.5699 |  |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0
4500rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 4500rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2
| Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0 |  | Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8
Thermo OFF set temperature | -25 | 41.7036 | 39.5611 | 32.1978 | 32.1978 | 26.8727 |  | Thermo OFF set temperature | -25 | 0 | 0 | 0 | 0 | 0 | 0
| -20 | 41.6506 | 39.6433 | 32.7765 | 32.7765 | 27.8427 |  |  | -20 | 0 | 0 | 0 | 0 | 0 | 0
| -15 | 45.8181 | 44.1721 | 37.0401 | 37.0401 | 30.8363 |  |  | -15 | 0 | 0 | 0 | 0 | 0 | 0
| -10 | 46 | 46 | 36.7852 | 36.7852 | 33.4411 |  |  | -10 | 0 | 0 | 0 | 0 | 0 | 0
| -5 | 46 | 46 | 36.915 | 36.915 | 34.3054 |  |  | -5 | 0 | 0 | 0 | 1 | 1 | 0
| 0 | 46 | 46 | 37.31 | 37.31 | 34.766 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 46 | 46 | 38.43 | 38.43 | 35.666 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0
5600rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 5600rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2
| Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0 |  | Amount of additional oil(g) | 430 | 190 | 0 | 430 | 190 | 0
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8
Thermo OFF set temperature | -25 | 43.5145 | 41.8682 | 36.5849 | 36.5849 | 32.5531 | 16.3637 | Thermo OFF set temperature | -25 | 0 | 0 | 0 | 0 | 0 | 0
| -20 | 43.356 | 41.8047 | 36.8904 | 36.8904 | 33.1116 | 16.6288 |  | -20 | 0 | 0 | 0 | 0 | 0 | 0
| -15 | 46 | 45.9459 | 41.572 | 41.572 | 37.5029 | 17.3068 |  | -15 | 0 | 0 | 0 | 0 | 0 | 0
| -10 | 46 | 46 | 44.7367 | 44.7367 | 36.9384 | 24.6686 |  | -10 | 0 | 0 | 0 | 0 | 0 | 0
| -5 | 46 | 46 | 45.2076 | 45.2076 | 36.9787 | 29.2181 |  | -5 | 0 | 0 | 0 | 1 | 1 | 0
| 0 | 46 | 46 | 45.5082 | 45.5082 | 37.3362 | 30.3183 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 46 | 46 | 45.8 | 45.8 | 43.4907 | 31.6481 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0
1
2

## d-explanation (hidden)
Judgment of ambient temperature at which oil can be returned | [7 empty] | Available operating conditon | [7 empty] | Output
2200rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 2200rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | Evaporator unit (≦2.0L/unit) |  | 1 | 2
| Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None |  | Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None | Oil return control set value | 2200rpm | Showed output on "Calculation sheet"
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | 3000rpm
Thermo OFF set temperature | -25 | Ambient temperature at which oil can be returned (No good oil returen on Blank condition) | [5 empty] | Thermo OFF set temperature | -25 | Showed operatable point by "1". | [6 empty] | 4500rpm
| -20 | [7 empty] | -20 | [7 empty] | 5600rpm
| -15 | [7 empty] | -15
| -10 | [7 empty] | -10
| -5 | [7 empty] | -5
| 0 | [7 empty] | 0
| 5 | [7 empty] | 5
3000rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 3000rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2
| Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None |  | Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8
Thermo OFF set temperature | -25 | Ambient temperature at which oil can be returned (No good oil returen on Blank condition) | [5 empty] | Thermo OFF set temperature | -25 | Showed operatable point by "1".
| -20 | [7 empty] | -20
| -15 | [7 empty] | -15
| -10 | [7 empty] | -10
| -5 | [7 empty] | -5
| 0 | [7 empty] | 0
| 5 | [7 empty] | 5
4500rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 4500rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2
| Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None |  | Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8
Thermo OFF set temperature | -25 | Ambient temperature at which oil can be returned (No good oil returen on Blank condition) | [5 empty] | Thermo OFF set temperature | -25 | Showed operatable point by "1".
| -20 | [7 empty] | -20
| -15 | [7 empty] | -15
| -10 | [7 empty] | -10
| -5 | [7 empty] | -5
| 0 | [7 empty] | 0
| 5 | [7 empty] | 5
5600rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2 |  |  | 5600rpm | Evaporator unit (≦2.0L/unit) | 1 |  |  | 2
| Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None |  | Amount of additional oil(g) | 430g | 190g | None | 430g | 190g | None
| Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8 |  | Refrigerant flow velocity(m/s) | 2 | 2.5 | 4 | 4 | 5 | 8
Thermo OFF set temperature | -25 | Ambient temperature at which oil can be returned (No good oil returen on Blank condition) | [5 empty] | Thermo OFF set temperature | -25 | Showed operatable point by "1".
| -20 | [7 empty] | -20
| -15 | [7 empty] | -15
| -10 | [7 empty] | -10
| -5 | [7 empty] | -5
| 0 | [7 empty] | 0
| 5 | [7 empty] | 5
1 | ← For data entry
2